CSPC · ICTU  —  SERVER ROOM MONITORING

SENSOR BOX — QUICK GUIDE

Keep this card on the box. Everything here is done from the dashboard or with a screwdriver. No laptop, no programming. Full setup: SENSOR-SETUP-SHEET.md.

# 1.  What the light means

## Starting up — first 30 seconds

| Light | Meaning |
| --- | --- |
| Blue, dim | Booting. Wait about 20 seconds |
| Magenta | Press BOOT now if you want to change the WiFi — 4 seconds only |
| Red | WiFi failed — wrong password, or network not found |
| Orange | On WiFi, but the server did not answer — Backend IP is wrong |
| Green | Connected. Nothing to do |

## Running

| Light | Meaning |
| --- | --- |
| Green | Normal |
| Green + blue blink every 5 s | Readings are not reaching the dashboard. Nothing is lost — they are saved on the memory card |
| Blue, bright | Room too cold |
| Yellow | Warning — heat, humidity or gas rising |
| Orange | Humidity critical |
| Red | Critical — heat or smoke. Buzzer is on |

Buzzer: one continuous tone = smoke. Fast beeping = heat or humidity critical. Slow beeping = warning. The blue blink never covers an alarm.

# 2.  Add a smoke sensor (MQ-2)

4 channels, 2 are fitted. CH is what the dashboard calls them — the GPIO column is only for whoever wires it.

| CH | Wire AOUT to | Printed on the board |
| --- | --- | --- |
| 1 | GPIO 34 | 34 — fitted |
| 2 | GPIO 35 | 35 — fitted |
| 3 | GPIO 36 | VP |
| 4 | GPIO 39 | VN |

- Unplug the box.

- Wire it: VCC → 5V, GND → GND, AOUT → that CH’s pin through the 10k / 20k divider.

- Plug in, wait for green.

- Dashboard → Environment → Add smoke sensor (admin).

- Pick the CH you wired, give it a location name, save.

- Press Recalibrate gas — only when the air is clean.

Never wire AOUT straight to the board. The sensor puts out 5 V, the pin takes 3.3 V. The channel stays off until step 5 — an empty pin picks up noise that can read as smoke. To remove a sensor: same screen → Remove sensor.

# 3.  Add an IR transmitter (aircon)

4 channels, 2 are fitted. CH is what the dashboard calls them.

| CH | Wire the signal pin to | Status |
| --- | --- | --- |
| 1 | GPIO 25 | fitted |
| 2 | GPIO 33 | fitted |
| 3 | GPIO 32 | free |
| 4 | GPIO 15 | free |

- Unplug the box.

- Wire it: VCC → 5V, GND → GND, DATA → that CH’s GPIO.

- Aim it at the aircon’s remote sensor — clear line of sight, like pointing a remote.

- Plug in, wait for green.

- Dashboard → Air Conditioner → Add Aircon (admin).

- Pick the CH you wired, name the unit, save.

The transmitter does nothing until step 6.

# 4.  Change a setting

| What | Where |
| --- | --- |
| WiFi / Backend IP | On the box — section 5 |
| Alarm levels (temperature, humidity, gas) | Dashboard → Alert Rules (admin) |
| When the aircon kicks in | Dashboard → Air Conditioner → Auto-Cooling Thresholds (admin) |
| Smoke baseline, after moving the box | Dashboard → Environment → Recalibrate gas |
| Device secret | Firmware — call the dev team |

No reflash needed except the last one. Changes reach the box in seconds.

# 5.  Change the WiFi or server address

- Plug the box in — do not touch any button yet.

- After about 4 seconds the light turns magenta.

- While it is magenta, press BOOT once (marked BOOT or IO0).

- On your phone, join the WiFi CSPC-ICTU-Sensor-XXXX (no password). The setup page opens by itself — if not, go to http://192.168.4.1.

- Configure WiFi → pick the network (2.4 GHz only), type the password, enter the Backend IP and port 3000.

- Save, and wait for the page to say Connected.

Do not hold BOOT while plugging in. That puts the chip in programming mode and it stops running. Unplug and start again.

# 6.  Never

- Wire anything while the box is plugged in.

- Wire an MQ-2 AOUT straight to the board — use the divider.

- Hold BOOT while powering on.

- Remove the coin cell from the clock module.

- Use a 5 GHz WiFi network.

- Use any pin not listed on this card.

# 7.  If something is wrong

| You see | Do this |
| --- | --- |
| Orange at startup | Backend IP wrong → section 5 |
| Red at startup | Wrong password, or a 5 GHz network → section 5 |
| Blue blink for a long time | Server or network is down. Readings are safe on the card |
| New sensor reads nothing | Not added on the dashboard → section 2, step 4 |
| New sensor reads a strange high value | Recalibrate gas in clean air |
| Aircon does not respond | Check the aim, and that the unit is registered → section 3 |
| Box never appears on the dashboard | Section 5, and check the server is running |

Anything else — contact ICTU or the development team.