# Circuit Diagram

Environment Monitoring Device · CSPC-ICTU Server Infrastructure Monitoring System · October 2026

# 1. Overview

This is the wiring diagram of the environment monitoring device: an ESP32 on an expansion shield, connected to one DHT22, four MQ-2 smoke sensors, four IR transmitters, a buzzer, a 16-LED WS2812B strip, a DS3231 clock, a micro SD card module and a Wi-Fi setup button. The diagram is on the next page; the table below lists each connection.

The physical layout of the box is in the separate Hardware Schematic document.

# 2. Pin connections

| Component | Pin | ESP32 pin | Notes |
| --- | --- | --- | --- |
| DHT22 | DATA | GPIO4 | VCC → 3.3 V (V row) |
| MQ-2 #1 | AO | GPIO34 | Through 10 kΩ / 20 kΩ divider · VCC → 5V |
| MQ-2 #2 | AO | GPIO35 | Through its own divider · VCC → 5V |
| MQ-2 #3 | AO | VP (GPIO36) | Through its own divider · VCC → 5V |
| MQ-2 #4 | AO | VN (GPIO39) | Through its own divider · VCC → 5V |
| IR TX #1 | S | GPIO25 | IR channel 1 |
| IR TX #2 | S | GPIO33 | IR channel 2 |
| IR TX #3 | S | GPIO32 | IR channel 3 |
| IR TX #4 | S | GPIO15 | IR channel 4 |
| Passive buzzer | + | GPIO26 |  |
| WS2812B LED ×16 | DIN | GPIO27 | 5V → shield 5V pin |
| DS3231 RTC | SDA / SCL | GPIO21 / GPIO22 | I2C · VCC → 3.3 V |
| Micro SD card | CS / SCK / MISO / MOSI | GPIO5 / 18 / 19 / 23 | SPI · VCC → 5V |
| Wi-Fi portal button | one leg | GPIO13 | Other leg → GND (internal pull-up) |

# 3. Power

- Supply: wall adapter → Mini UPS (5 V 2 A) → USB-C input on the ESP32 shield.

- 5 V: MQ-2 sensors, WS2812B strip and micro SD module, from the shield's 5V pin.

- 3.3 V: DHT22 and DS3231, from the shield's V rows (jumper set to 3.3 V).

- GND: common to every module.

# 4. Key notes

- Voltage dividers: each MQ-2 outputs up to 5 V, so AO → 10 kΩ → ESP32 pin, with 20 kΩ from that pin to GND, brings it to 3.3 V.

- VP and VN are input-only: fine for MQ-2 #3 and #4, but they cannot drive an IR transmitter.

- New MQ-2 channels are not read until enabled on the Environment page.

Figure 1. Circuit diagram of the environment monitoring device